This Consultant’s Specification has been produced by Hochiki Europe (UK) Limited for use by Fire System Consultants preparing specifications for the design and supply of life safety systems.

# Scope of Work

To design, supply and install an Analogue Addressable Fire Alarm Control System in accordance with the details specified herein and in accordance with supplied drawings.

The HFP fire alarm system shall include all materials, equipment and wiring required to install the complete Fire Detection and Alarm System. The system shall include but not be limited to one or more control panels, repeater panels, and sensors, call points, audible and visual alarm indicating devices and relays.

The installation shall include the provision of all cables required for connection of the detection, alarm indicating and other devices along with connections to the power supply as appropriate to the design. All cabling shall conform to the requirements and recommendations of the HFP Fire Alarm Control Panel manufacturer and British Standard 5839-2013.

The system shall be designed such that no more than 90% of the available signalling / detection loop capacity is employed to allow for future requirements.

# Standards

The fire detection system shall be designed, installed and commissioned in accordance with, and all elements shall meet the requirements of BS5839 Part 1: 2013 Code of Practice and EN54-Part 2: 1998.  The responsible company should be able to demonstrate their competence to design, install and commission the HFP system, e.g. by certification to BAFE SP203, LPS1014 or other relevant standard and must be an approved Hochiki Systems Partner (HSP).

The equipment manufacturer shall operate a quality management system in accordance with ISO 9001:2000. In addition, the equipment shall be manufactured under a recognised factory control procedure such as the BSI Kitemark scheme.

All detection devices shall be independently certified as complying with the relevant EN54 standard.

# Analogue Addressable Fire Alarm Control Panel (FACP)

## Functional Description

The fire alarm control panel (FACP) shall be the central processing unit of the system, receiving and analysing signals from fire sensors, providing audible and visual information to the user, initiating automatic alarm response sequences and providing the means by which the user interacts with the system.

The FACP shall be certified as meeting the requirements of EN54-2 and EN54-4 by a suitable, notified body.  A certificate and test report shall be made available for inspection as evidence of certification.

The FACP shall be easily configurable to meet the exact detection zone and output mapping requirements of the building.

The FACP shall be microprocessor based and operate under a multitasking software program. Operating programs and configuration data shall be contained in re-configurable non-volatile memory.  Retention of the memory shall not rely on any form of battery or capacitor back-up device.  The FACP shall incorporate separate processors for loop processing and central processing.

Provision shall be made for each addressable loop to be sub-divided into geographical zones.   The section of wiring corresponding to each zone circuit shall be protected from faults in other sections by line isolator modules.

In order to facilitate re-configuration and system extension, the allocation of addresses to devices shall be independent of their physical arrangement on the loops.

Up to 127 individually addressed standard devices shall be configured on each addressable loop. Loop powered sounders incorporated as a sensor bases shall be available.

The FACP shall have the capability to support sub-addressing of addressable modules so that the support of 8 inputs and 8 outputs from one loop address is provided. Inputs and Outputs should be controlled independently.

It shall be possible to fit a 40-column printer to the FACP which will print system events automatically and logged data upon request.

The FACP shall incorporate a real time clock to enable events to be referenced against time and date.

## Additional Components

It shall be possible to fit the FACP with a network board to allow up to sixty-four control panels to communicate with each other.  The network shall be fully fault tolerant and shall continue to function normally under any single fault condition.

It shall be possible to fit the FACP with up to 32 Fire alarm repeater panels, these shall be connected via a four-core cable carrying power and serial data.

It shall be possible to fit up to thirty-two, sixteen-way input/output modules, 8-way relay modules, 6-way sounder modules or 4-way conventional zone modules or any combination thereof to each control panel.  Modules shall connect to a separate serial bus but shall be programmable in the same manner as devices connected to the addressable loops.

Once connected and accepted by the FACP, removal or disconnection of any Fire alarm repeater, ancillary board or sounder board shall be announced as a fault condition at the FACP.

It shall be possible to fit the FACP with a modem board to allow remote interrogation and monitoring of a network of control panels.

## Configuration

It shall be possible to perform configuration updates on site using a portable personal computer and a windows-based configuration utility.  This facility shall allow the following parameters to be set:

### System

Produce a configuration file which contains data for up to 64 panels connected together as a network.

Set cause and effect tables for any device to operate devices or functions on any panel or panels connected to the network.

Upload and view graphically the configuration from a single panel or entire network of panels.

### Control Panel

Panel name (network identity, fifteen characters minimum)

Panel text (comfort message or service company 40-characters minimum)

Change code numbers for access levels two and three.

Select sounder ringing mode as common, zonal or two stage

Select first and second stage delay times for each sounder output to between zero and five minutes.

Set number of loops on panel as one, two or four

Set number of zones on panel as 0,16, 48 or 96

Set loop sounder volume globally

Set start and end times for day night mode for each day of the week

### Detectors

Allocate a zone

Set a delay before the panel responds to a fire signal

Indicate pre-alarm

Set day sensitivity and night sensitivity separately

Address loop powered base sounders

Allocate a 40-character location text message.

### Call points

Allocate a zone

Allocate a 40 character location text message

### Switch units (input)

Allocate a zone for each input and the device itself

Define input action as fire, faulty, pre-alarm, evacuation, alert, security alarm, silence alarm, reset, transparent, disablement or test mode.

Change the input action message from the default to any one of the above or to any one of a user defined library of 10 additional action messages.

Set a delay before the panel responds to a fire signal

Select whether the input requires the control panel to be reset or is self-clearing upon removal of the input.

Allocate a 40-character location text message

### Relay or sounder units (output)

Allocate a zone for each input and the device itself

Define whether the device responds to evacuate inputs, as a sounder (default ringing), is silenceable, needs to be reset or produces a single pulsed operation of between one and five seconds (programmable)

Has a delay before operating (zero to five minutes)

Allocate a 40-character location text message

### Loop powered sounders

Allocate a zone

Define whether the device responds to evacuate input, as a sounder (default ringing) is silenceable, needs to be reset or produces a single pulsed operation of between one.

Has a delay before operating (zero to five minutes)

Allocate a 40-character location text message.

## Panel Construction

The housing containing the FACP shall be of metal construction and shall be capable of being surface or semi-flush mounted. It shall be complete with cable knocks-outs in sufficient quantity to accommodate all likely cabling requirements.

The housing shall afford a minimum ingress protection to IP30 and it shall not be possible to open the FACP without the use of a special tool or key.

## Panel Indications

The FACP shall monitor the status of all devices on the addressable loops for fire, short-circuit fault, open-circuit fault, incorrect addressing, unauthorised device removal or exchange, pre-alarm condition and contaminated detector condition.

The FACP shall also monitor the status of internal connections and interfaces including charger and batteries.

The FACP shall provide the following discrete visual indications:

| POWER ON | Green LED Indicator |
| --- | --- |
| FIRE ALARM | Red LED Indicator |
| PRE-ALARM | Yellow LED Indicator |
| ON TEST | Yellow LED Indicator |
| BUZZER SILENCED | Yellow LED Indicator |
| DELAY ACTIVE | Yellow LED Indicator |
| MORE EVENTS | Yellow LED Indicator |
| GENERAL DISABLEMENT | Yellow LED Indicator |
| GENERAL FAULT | Yellow LED Indicator |
| POWER FAULT | Yellow LED Indicator |
| SYSTEM FAULT | Yellow LED Indicator |
| SOUNDER FAULT/DISABLED | Yellow LED Indicator |

## Display

In addition to the indications above, the FACP shall have an integral 240 x 64 pixel graphic LCD display.

The display shall incorporate a backlight which will illuminate upon any event (excluding mains failure) or button press.

The display shall be capable of simultaneously indicating the number of outstanding events and their types as well as the current event.

## Panel Controls

The panel shall be provided with at least the following manual controls:

| SILENCE BUZZER | LAMP TEST |
| --- | --- |
| ACKNOWLEDGE ALARM | MORE FIRES |
| RE-SOUND ALARM | MORE EVENTS |
| RESET | HELP |
| MENU NAVIGATION PAD (UP, DOWN, LEFT, RIGHT, ENTER, EXIT) |  |

## Remote Monitoring Signals

The FACP shall contain at least three programmable inputs to allow interconnection to other systems.

The FACP shall contain at least two programmable outputs to allow interconnection to other systems.

The FACP shall be capable of monitoring and controlling remote site devices, such as relays for the control of plants and dampers directly from the addressable loops.

The FACP shall be capable of monitoring fire doors such that, in the event of a fire alarm condition, an event is generated to warn of the failure of a fire door to close.

## Software

The FACP shall have, as a standard software enhancement, the ability to annunciate a pre-alarm condition designed to give the earliest possible warning of potential fire condition without raising the full alarm condition.

The FACP shall have as a standard software enhancement the ability to automatically adjust the alarm threshold levels to compensate for changes in detector sensitivity due to contamination over a period of time.

The FACP shall have, as a standard software enhancement, the ability to provide an indication that a detector is nearing a level of contamination, which requires that it be replaced or serviced.

The FACP shall have, as a standard software enhancement, the ability to provide automatic warning that a detector has reached a level of contamination, which requires that it be replaced or serviced.

The FACP shall have, as a standard software enhancement, the ability to synchronise loop data transmission to eliminate the possibility of data corruption due to cross-talk or similar effects.

The FACP shall have, as a standard software enhancement, extensive, context sensitive help screens to offer additional information on system status at all times.

## Sounder Connections

The FACP shall provide the necessary outputs to separately operate a minimum of two monitored circuits of common system sounders. Each output shall be capable of driving a sounder load of up to 1A.

The FACP shall also be able to monitor the integrity of and control standard sounder circuits, via a suitable addressable module.

The FACP shall be capable of providing a two-stage alarm sounder facility that can be programmed, either on a zonal basis or common system basis, to meet the requirements of the fire authority. Sounder outputs shall be available as follows:

Alert, intermittent pulsed tone

Evacuate, continuous tone

The FACP shall have the facility to change, on a per sounder zone basis, the sound output dependent upon whether the source of alarm is:

An automatic detector, e.g. smoke, heat

A manual call point

The FACP shall have the facility to generate a slow pulsed output to all sounder circuits in response to a security alert input.

## Fault Reporting

The FACP shall monitor all critical system components and interconnections, internal and external, such that a failure, which would prevent the correct operation of the alarm functions, causes the FAULT indicator to light and a message to be given on the alphanumeric display within 60 seconds of occurrence.

The following faults shall be reported in the manner described above:

Loop Short Circuit

Loop Open Circuit

Unconfigured Device

Device Missing

Addressable Device Failure

Incorrectly Configured Device

System Fault (Processor)

Low Battery

Charger Failure

Earth Fault Monitoring

Battery Fault

Mains Failure

Sounder Wiring Open Circuit (Per Circuit)

Sounder Wiring Short Circuit (Per Circuit)

To help fault finding and repair, the FACP shall provide text messages to indicate the location of where a fault has occurred in the system.

## System Management

The FACP shall incorporate the following system management facilities:

Isolate/re-connect individual outputs or inputs of addressable points

Isolate/re-connect individual zones

Isolate/re-connect individual loops

Isolate/re-connect individual sounder circuits

Isolate/re-connect all volt-free contacts individually

Isolate/re-connect panel inputs

Walk-test of a selected zone to verify detectors and sounders

View system status

Print event log

Print point status

Set time

View contamination status

Access to the facilities describe above shall be restricted to user Engineer level or above.

The FACP shall have an event log capable of storing the last 500 events that have occurred. It shall be possible to view the content of the log via the alphanumeric display. Events shall be displayed in chronological order with the newest events first. It shall be possible to scroll through the events.

The FACP shall be designed so that, for each type of analogue addressable detector, the overall response time including the sensor, the signal transmission system and the fire decision algorithm, meets the requirement of European Standards.

The FACP shall be capable of isolating a group of selected detectors in areas of the building where maintenance work is carried out.

# Addressable Devices

## Basic Sensor Requirements

The manufacturer shall have available the following types of analogue addressable automatic sensors, for direct connection to the system addressable loops, these analogue sensors shall be addressed using a hand-held programmer:

Optical smoke sensors

Heat sensors

Multi-sensors

## Other Addressable Units

The manufacturer shall be capable of offering two-state addressable versions of the following units, taking only one address from the loop:

Optical smoke sensors

Heat sensors

Multi-sensors (heat and smoke)

Multi-sensors (heat, smoke and CO)

Optical beam smoke detectors

Conventional detector interface module

Sounder control modules

Relay interface modules

Switch monitoring modules

Loop powered base and wall sounders

Loop powered visual devices such as beacons and remote indicators

Manual call points for indoor use

Manual call points for outdoor use

Analogue addressable sensors and modules must be able to transmit to the FACP an address to be used in the system configuration.

It must be possible to connect and mix addressable sensors, addressable manual call points and addressable modules within the same zone sub-division of an addressable loop.

All equipment connected to the system addressable loop, either directly or via interfaces, shall be proofed against electrical noise, high frequency pulses and electromagnetic influences from other equipment.

The manufacturer shall have available suitable equipment to test and remove or exchange all three main types of automatic point-type sensors when installed.

## Sensors - General

All three sensors types (Optical, Heat and Multi) should be available in these variants:

- With Marine approval

- With SIL Level 2 approval

- With integrated short-circuit isolator

All sensors should also incorporate a locking mechanism, utilised by removing a plastic tab from the underside of the sensor, which once locked onto the base means the sensor can only be removed with a special removal tool.

All sensors shall be designed to have high resistance to contamination and corrosion and shall include RFI screening to minimise the effect of radiated and conducted electrical interference.

All sensors shall incorporate two LEDs, clearly visible from the outside, to provide indication of status.  The LEDs should be controlled from the FACP if the LEDs flash during the normal polling sequence.  The LED colour shall indicate status:

| Green - blinking | Polling (communicating with FACP) |
| --- | --- |
| Amber - solid | Active short-circuit isolation (for SCI variants only) |
| Red - solid | Alarm condition |

In locations where the sensor is not readily visible, remote indicator units shall be provided.

## Optical Smoke Sensor

The design of the point-type photoelectric smoke detector sensing chamber shall be optimised to minimise the effect of dust deposit over a period of time.  The chamber cover shall be removable for ease of cleaning or replacement and shall incorporate a screen designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).

## Multi-Sensor

The multi-sensor offering should consist of a model either capable of monitoring the environment with two different sensing elements or a model with three different sensing elements:

| 2 Sensing Elements | 3 Sensing Elements |
| --- | --- |
| Optical (for smoke) | Optical (for smoke) |
| Thermal (for heat) | Thermal (for heat) |
|  | Carbon Monoxide (CO) |

The design of the smoke sensing chamber of the multi-sensor shall be optimised to minimise the effect of dust deposit over a period of time.  The chamber cover shall be removable for ease of cleaning or replacement and shall incorporate a screen designed to prevent all but the very smallest of insects from entering the sensing chamber, (50 holes per square centimetre or more).

The 3-sensing element multi-sensor should be able to operate in a minimum of 24 EN approved operating modes, using various combinations of each sensing element, that can be matched to the installation environment.  The multi-sensor CO sensing cell should have a manufacturer’s guaranteed life span of 10 years.  The multi-sensor should feature software enhancements to reduce false alarms.

The modes of the multi-sensor should be controlled by the FACP, when the FACP changes from one mode to another the FACP should re-calibrate the multi-sensor.

The multi-sensor should have the capability of monitoring any of the sensing elements, if either of the elements fail it should be reported and displayed at the FACP.

## Heat Sensor

The heat detectors shall be capable of detecting rapid rise in temperature and/or fixed absolute temperatures.

The heat detectors shall employ two heat-sensing elements with different thermal characteristics to provide a rate of rise dependent response.

The heat sensor shall meet he requirements of a Class P heat sensor.

## Mounting Base

All sensors shall be fixed in place by means of a mounting base that allows devices to be twist-fitted.  The base must be electronics-free.  This shall enable insulation and continuity checks to be completed on the wiring with the detector heads removed.

The base should be capable of supporting sensors, beacons, remote indicators, sounders and sounder/beacons without the need to physically change base types.

In the case of the integrated SCI variant sensors, the base must provide and maintain the short-circuit functionality.

Termination facilities shall be available for earthing.

# Other Devices

## Optical Beam Smoke Sensor

The addressable beam smoke detector should be of a reflective type and be able to provide a detection range of between 5 m and 100 m in detection length with a 15 m width (maximum coverage of 1500 m²).

The unit should be loop-powered and be capable of continually and automatically correcting its alignment without intervention.  Ideally, the detector head should be commissioned and controlled from ground level utilising a control unit to avoid working at height.

## Manual Call Points

The addressable manual call points shall monitor and signal to the FACP the status of a switch operated by a “non-frangible element” assembly. They shall be red in colour and suitable for surface or flush mounting.  The addressable call points shall be provided with an integral red LED to indicate activation.  The polling LED can be switched off from the FACP.

One version of the addressable call point shall be available mounted in a weatherproof housing, affording protection to IP 66.

The addressable call points shall be capable of operating by means of thumb pressure and not require a hammer.  They shall be capable of being tested using a special ‘key’ and feature a non-frangible, resettable element instead of a glass.

The addressable call points shall incorporate a mechanism to interrupt the normal addressable loop scan to provide an alarm response within 3 seconds and shall be field programmable to trigger either an alert or an evacuate response from the FACP.

The unit should also be available as an integral SCI (short-circuit isolator) variant, both for internal and external use.

## Loop Powered Beacon

The addressable Beacon is a visual indicating device that can be fitted onto the Isolator base or Standard Base.

The beacon shall have its address programmed via a hand-held address tool, and the lens should be available in red, blue or amber with a flash rate of 0.5 Hz or 1 Hz.

The Beacon should also incorporate a locking mechanism, this is utilised by removing a plastic tab from the underside of the beacon.  Once locked onto the base, the beacon can only be removed with a special removal tool as per a sensor.

## Sounder Controller Module

The addressable sounder module shall be capable of monitoring and controlling two independent circuits of alarm sounders using a single loop address.

24 VDC power to drive the sounders shall be derived independently from the FACP.

The addressable sounder module shall be capable of operating both sets of sounders in a pulsing or continuous mode as determined on the module. Each circuit shall be individually programmable. Sounder circuits shall be capable of synchronisation.

The addressable sounder module shall provide the facility to monitor the wiring to the sounders for open or short-circuit and transmit the necessary fault signal to the FACP. Each sounder circuit shall be separately fused.

The addressable sounder module shall provide the facility to monitor for failure of the power supply for the sounders and transmit the necessary fault signal to FACP.

The addressable sounder module shall provide a green LED indication when the FACP is polling it.

The addressable sounder module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Powered Output Module

The addressable powered output module shall incorporate two monitored inputs and have a 24 Vdc output with selectable current levels, these should range from 2 mA to 32 mA (in 2 mA increments) the module should use a single loop address, and the current levels should be programmed from the FACP.

The unit should be addressed electronically using a hand-held tool and special lead

## Single Input Module

The addressable single input module shall incorporate one monitored input and be designed to connect to the loop via a terminal block.

The unit should be addressed electronically using a hand-held tool and special lead.

## Dual Zone Conventional Detector Interface Module

The conventional detector interface module shall be capable of monitoring two independent zones, each of up to 30 conventional detectors using a single loop address.

24 VDC power to power the conventional detectors shall be derived independently from the FACP.

The conventional detector interface module shall provide the facility to monitor the detector zones for open or short-circuit and transmit the necessary fault signal to the FACP.

The conventional detector interface module shall provide two remote LEDs to indicate which zones are in alarm and shall provide a red LED to indicate FACP polling.  The unit should also support Schottky Diode head removal.

The conventional detector module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Single Zone Conventional Detector Interface Module

The conventional single zone detector interface module shall be capable of monitoring one independent zone of up to 6 conventional detectors using a single loop address.

The conventional single zone detector interface module should be loop-powered.

The conventional single zone detector interface module shall provide the facility to monitor the detector zone for open or short-circuit and transmit the necessary fault signal to the FACP.

The conventional single zone detector interface module shall provide a remote LED facility to indicate when the zone is in alarm and shall provide a red LED to indicate FACP polling.  The unit should also support Schottky Diode head removal.

The conventional single zone detector interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Intrinsically Safe Compatible Conventional Detector Interface Module

The Intrinsically safe conventional detector interface module shall be capable of monitoring two independent zones, each of up to 20 intrinsically safe conventional detectors using a single loop address.  This module should be used in conjunction with galvanic isolators or Zener barriers.

24 VDC power to power the conventional detectors shall be derived independently from the FACP.

The Intrinsically safe conventional detector interface module shall provide the facility to monitor the detector zones for open or short-circuit and transmit the necessary fault signal to the FACP.

The Intrinsically safe conventional detector interface module shall provide two remote LEDs to indicate which zones are in alarm and shall provide a red LED to indicate FACP polling.

The intrinsically safe conventional detector interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Relay Controller Module

The addressable relay interface module shall be capable of switching two independent relays; either normally open or normally closed, each rated at 30 V, 1 Amp.

A single input shall provide open and short circuit monitoring facilities, set locally at the unit.

The addressable relay interface module shall use a single loop address.

The unit shall be powered directly from the addressable loop.

The addressable relay interface module shall provide an LED indication when the FACP is polling it.

The addressable relay interface module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

Ideally, to save space during installation a DIN rail alternative model should be available.

## Mains Relay Controller Module

The addressable mains relay controller module shall be capable of switching one relay; either normally open or normally closed, rated at 250 V, 5 Amps.

A single input shall provide open and short circuit monitoring facilities, set locally at the unit.

The addressable mains relay controller module shall use a single loop address.

The unit shall be powered directly from the addressable loop.

The addressable mains relay controller module shall provide an LED indication when the FACP is polling it.

The addressable mains relay controller module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Single Input Monitoring Module

The addressable switch monitoring module shall be capable of monitoring two independent voltage free contacts, each normally open or normally closed, using a single loop address.

The unit shall be powered directly from the addressable loop.

The addressable switch-monitoring module shall provide a red LED indication when the FACP is polling it. The LED shall be continuously lit when either input is active.

The addressable switch monitoring module shall feature a short-circuit isolator (SCI) as standard with a separate LED to indicate when the loop is in short-circuit.

To save space during installation a DIN rail alternative model should be available.

## Short Circuit Isolator Base

The short circuit isolator base shall provide protection on the addressable loop by automatically disconnecting the section of wiring between two isolators where a short circuit has occurred.

The short circuit isolator base shall derive its power directly from the addressable loop.

Any Sensor or Beacon can be fitted to the isolator base; the isolator base is also ceiling or wall mountable.

## Loop Powered Sounder Beacon Base

Addressable electronic sounder beacon bases shall be connected directly to the detection loops.  These shall be able to be mounted onto a standard or short circuit isolator sensor mounting base.  An analogue smoke sensor, multi-sensor, heat sensor, addressable beacon or an addressable remote indicator may also be mounted onto the sounder beacon base, if required.  The sounder beacon base shall be ceiling or wall mountable.  A cover plate shall be fitted when no other device is to be fitted on the sounder beacon base.

The address of sounders used as sensor bases shall be set automatically at the FACP.  This will be above 127 so as not to restrict the number of other addressable devices on the loop.

The loop-powered sounder beacon base volume and tone shall be determined at the FACP.  The loop powered sounder beacon base shall be programmable to have a sound output variable between 50 dB(A) and 98 dB(A) (±2 dB(A)) at 1 metre distance and have a maximum current draw of between 0.8 mA and 21 mA with both sounder and beacon activated simultaneously.  The beacon should employ LED technology to reduce current consumption and maintenance.

The sounder and beacon within the device should have the capability to be operated separately or together, this should be selected at the FACP.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 compatible tones.

Where recommended by the risk assessment, an EN54-23 compliant variant should be available for certain environments.

## Loop Powered Sounder Base

Addressable electronic sounder bases shall be connected directly to the detection loops.  These shall be able to be mounted onto a standard or short circuit isolator sensor mounting base.  An analogue smoke sensor, multi-sensor, heat sensor, addressable beacon or an addressable remote indicator may also be mounted onto the sounder base, if required.  The sounder base shall be ceiling or wall mountable.  A cover plate shall be fitted when no other device is to be fitted on the sounder base.

The address of sounders used as sensor bases shall be set automatically at the FACP. This will be above 127 so as not to restrict the number of other addressable devices on the loop.

The loop-powered sounder base volume and tone shall be determined at the FACP. The loop powered sounder base shall be programmable to have a sound output variable between 50 dB(A) and 98 dB(A) (±2 dB(A)) at 1 metre distance and have a maximum current draw of between 0.8 mA and 16 mA.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 compatible tones.

## Loop Powered Wall Sounder

The Loop Powered Wall Sounder shall be connected directly to the loops where required. The unit shall be fixed onto a sounder specific mounting base which will be red to match the sounder.  A weatherproof kit should be available to increase the IP Rating of the wall sounder to IP66.

The Wall Sounder sound output should be variable between 90 dB(A) and 102 dB(A) (±2 dB(A)) and should have a maximum current draw of between 2 mA and 8 mA depending on the tone used.

An auto-shutdown facility should be available that minimises noise pollution by shutting the sounder down after a user-specified time limit.  The unit should be capable of producing all 51 (fifty-one) EN54 compatible tones.

## Loop Powered Wall Sounder Beacon

The Loop Powered Wall Sounder Beacon shall be connected directly to the loops where required.  The unit shall be fixed onto a sounder specific mounting base which will be red to match the sounder.  A weatherproof kit should be available to increase the IP Rating of the wall sounder to IP66.

The beacon lens should be transparent red and utilise LED technology to reduce current consumption and maintenance.

The Wall Sounder Beacon sound output should be variable between 90 dB(A) and 102 dB(A) (±2 dB(A)) and should have a maximum current draw of between 2 mA and 13 mA depending on the tone used and with both sounder and beacon activated simultaneously.

The sounder and beacon within the device should have the capability to be operated separately or together, this should be selected at the FACP.

The unit should be capable of producing all 51 (fifty-one) EN54 compatible tones.

Where recommended by the risk assessment, an EN54-23 compliant variant should be available for certain environments.

## EN54-23 Compliant Loop Powered Wall Beacon (VAD)

The loop-powered wall beacon should contain a free-form optic designed to produce a highly visible flash which should meet the cubic light volume coverage requirements of EN54-23.  The flash frequency should be 0.5 or 1 Hz at an operating voltage of 17 to 41 VDC.  The unit should fit directly onto the standard sensor mounting base and be available with either red or white LEDs.

## EN54-23 Compliant Loop Powered Ceiling Beacon (VAD)

The loop-powered ceiling beacon should contain a free-form optic designed to produce a highly visible flash which should meet the cylindrical light volume coverage requirements of EN54-23.  The flash frequency should be 0.5 or 1 Hz at an operating voltage of 17 to 41 VDC.  The unit should fit directly onto the standard sensor mounting base and be available with either red or white LEDs.

## Hand Held Address Programmer

This unit should be capable of electronically addressing analogue devices such as sensors, beacons, remote indicators, sounder bases, sounder/beacon bases and (with an optional lead) manual call points.  It should also be capable of listing six different fault codes relating to the device that is being programmed.  This programmer should also be capable of reading the device’s current analogue value.

## Voice Alarm Evacuation System

The voice alarm evacuation system comprising of rack-mounted units, speakers and microphones shall be fully compliant with BS5839 Part 8 (voice alarm systems).  The racks should be capable of interacting with the analogue fire system loop by way of a suitable control module.

The messages contained within the panel shall be digital recordings such as MP3s.  It should be possible to update the messages with a range of different languages.  The messages should consist of “evacuate”, “alert” and “test” types.

The system should feature two amplifiers.

The rack should feature an internal battery and the battery charger should be EN54 compliant.

Provision shall be made for the rack unit to interact with a background music source that can be interrupted whenever an “evacuate”, “alert” or “test” condition is activated.  The rack should also feature connections for both an emergency microphone (“Fireman’s Mic”) and a desk-top style microphone, both of which shall be able to interrupt the background music source in case of emergency services announcements.

## Air Sampling Smoke Detection System

The air sampling smoke detection system shall comprise detector units/panels featuring an internal fan which are connected to a sampling pipe (or a series of sampling pipes).  The detector unit shall continually sample the air in a particular area and by use of laser particle detection technology shall recognise the presence of airborne pollutants (smoke) at very low levels (High Sensitivity Smoke Detection).

The detector units should be capable of interacting with the analogue fire system loop by way of a suitable internally mounted control module.  The units shall also feature fire and fault relays for remote monitoring by the local fire detection system or a BMS system.

An RS485 communications bus should be provided as standard for networking several units together and for remote communications.

Several detection units shall be able to be controlled from one “command” unit.  This command unit shall be able to display information and control remotely the “slave” detection units.

## Alarm Bells

Fire alarm bells shall be under-dome type with a high resonance pressed alloy-steel gong to ensure a loud clear-tone ring.  They shall be fully suppressed and polarised.

The operating mechanism shall be fully enclosed, and the gong shall be red stove enamelled for long life.

Alarm bells shall have a minimum sound output of 95 dB (A) at 1 metre distance and shall have a maximum current consumption at 24 VDC of 30 mA.

## Wireless Fire Detection

The wired to wireless fire detection system shall be connected directly to the FACP loop using a loop-powered translation module.  The field devices should use bi-directional radio waves to communicate with the translation module, which should in turn communicate with the FACP allowing full control and monitoring of the wireless field devices.  The radio signal shall be self-optimising both in amplitude and frequency.  An automatic channel hopping facility should be included.  The system shall be expandable via the addition of expansion modules which shall boost the radio signals to the translation modules.  Field units shall utilise standard, low-cost lithium battery technology and, in accordance to EN54-25, contain two batteries – a primary and a secondary (back-up).

## Wired To Wireless Translation Module

The translation module should allow a wireless fire detection system to be interfaced directly onto the loop, with a total of 6 being permitted per loop.  It should be loop-powered and be able to support up to 32 wireless devices or up to 7 expansion modules (maximum of 5 child expansion modules connected in cascade (layer) or a maximum of 3 child expansion modules connected directly to the translation module or any one layer of an expansion module cascade).

## Wireless Expansion Module

The wireless expansion module should allow extended signal coverage for the wireless system by boosting signal strengths from translation modules, to cover larger buildings.  Up to 7 expansion modules can be supported by a single translation module (maximum of 5 child expansion modules connected in cascade (layer) or a maximum of 3 child expansion modules connected directly to the translation module or any one layer of an expansion module cascade).

## Wireless Conventional Interface Module

The wireless conventional interface module shall allow a zone of wireless devices to be added to an existing conventional zone (or as a stand-alone zone).  The zone should be wired directly to the wireless conventional interface module which then in turn can support an expansion module.

## Wireless Single Channel Input Module

The wireless single channel input module shall allow the on/off status (alarm/fault) of an external device to be transmitted to the FACP wirelessly via a wireless conventional interface module, a wireless expansion module or translation module.

## Wireless Powered Output Module

The wireless powered output module shall allow the FACP to activate/switch the circuits of an external device or system wirelessly via a wireless conventional interface module, a wireless expansion module or translation module.  The units contacts should be configurable to be normally open or normally closed and switch at 30 VDC/125 VAC at 2 A.  The unit should also be configurable to provide either a 12 VDC or a 24 VDC output.

## Wireless Manual Call Points

The wireless resettable manual call point shall feature a ‘non-frangible’ window element which when activated results in a plastic ‘flag’ being displayed in the window of the unit.  A supplied key will reset the flag and unit.  There should be a weatherproof version available for exterior use.

## Wireless Sensors

The wireless sensor range should consist of a photoelectric smoke sensor, a rate of rise heat sensor and a multi-criteria sensor (smoke and heat).  Each sensor shall feature a polling/activation LED.  The sensors should be EN54 compliant.  Sensors should be supplied with their own mounting bases.

## Wireless Wall Sounders

The wireless wall sounder range should consist of an internal wall sounder, an external (IP66) wall sounder, a wall sounder beacon and an external (IP66) wall sounder beacon.  The sound output of these devices shall range between a minimum of 6 dB(A) and a maximum of 100 dB(A).  The wall sounder beacons shall provide a flash rate/light output of 1 Hz / 1 Cd.

## Wireless Base Sounders

The wireless base sounder range should consist of a base sounder (audio) and a base sounder beacon (audio visual).  Both models in the range shall provide a maximum sound output of 90 dB(A).  The base sounder beacon shall also provide a flash rate of 1 Hz.  The bases shall provide a fixing for any wireless sensor.  The bases shall provide a fixing for a cover plate when a sensor is not utilised.

## Wireless Beacon

The wireless beacon shall provide two flash rates of 0.5 Hz or 1 Hz with a red lens.

# System Delivery

The specialist fire system contractor must be able to demonstrate competence by means of a valid manufacturer endorsed certificate relating to the products associated with this project.

The specialist fire system contractor must also be able to demonstrate competence by means of valid certification for technical accreditation by one of the following assessment bodies:

LPS1014

BAFE SP203

ECA / FSA Category A3

The accreditation must be specifically relevant to the specialist fire system contractor being positioned to certify their work in the following modules:

Design

Installation

Commissioning

Maintenance

Verification

# END OF SPECIFICATION

Hochiki Europe (UK) Ltd. reserves the right to alter the specification of its products from time to time without notice. Although every effort has been made to ensure the accuracy of the information contained within this document it is not warranted or represented by Hochiki Europe (UK) Ltd. to be a complete and up-to-date description.  Please check our web site for the latest version of this document